## OPTION 01
LT-WATSAN PROJECT
S/N | PROJECT SUMMARY - OPTION 01
KIGOMA OPTION
1 | KASEKE INTAKE
| Intake Capacity | 101,778 m3/day
a. Raw water pump station
| Operating time | 22hrs
| Raw water high-lift pump | H = 35 m, (2W+1S)@2,313 m3/h parallel, v = 1.16 m/s
| Raw water sump | V = 15,000 m3
| b. Raw water rising main to Kaseke WTP | Length (m)
| DI-DN1200-PN10 | 750
2 | KASEKE WTP
| WTP capacity | 94,653 m3/day
| Operating time | 22 hrs
| high-lift pump | H = 405 m, (6W+3S)@717 m3/h parallel, v = 1.057 m/s
| Clear water sump | V = 15,000 m3
3 | RISING MAIN FROM KASEKE WTP TO SIMBO JUNCTION | Length (m)
| DI-DN1200-PN40 | 2805
| DI-DN1200-PN50 | 14390
Sub-total
4 | RISING MAIN FROM SIMBO JUNCTION TO SIMBO ST | Length (m)
| DI-DN450-PN16 | 395
| DI-DN450-PN25 | 895
| DI-DN450-PN30 | 305
| DI-DN450-PN40 | 235
Sub-total
| Simbo storage tank | 3,000 m3
5 | RISING MAIN FROM SIMBO JUNCTION TO RUSESA BPS | Length (m)
| DI-DN1200-PN10 | 5376
| DI-DN1200-PN16 | 3159
| DI-DN1200-PN25 | 12178
| DI-DN1200-PN30 | 4585
| DI-DN1200-PN40 | 5143
Sub-total
6 | RUSESA BPS
a. Rusesa booster station BPS
| High-lift pump | H = 330 m, (6W+2S)@629 m3/h parallel, v = 0.927 m/s
| Sump capacity | V = 12,000 m3
| Operating time | 22 hrs
| b. Rising main from Rusesa BPS to Rusesa ST | Length (m)
| DI-DN1200-PN10 | 298
| DI-DN1200-PN16 | 279
| DI-DN1200-PN25 | 280
| DI-DN1200-PN30 | 2390
| DI-DN1200-PN40 | 1935
Sub-total
| Rusesa storage tank | 20,000 m3
7 | GRAVITY MAIN FROM RUSESA ST TO NYUMBIGWA JUNCTION | Length (m)
| DI-DN1000-PN10 | 400
| DI-DN1000-PN16 | 230
| DI-DN1000-PN25 | 20960
| DI-DN1000-PN30 | 3730
Sub-total
8 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO MASANZA UVINZA | Length (m)
| DI-DN500-PN16 | 1145
| DI-DN500-PN25 | 20818
| DI-DN500-PN30 | 14110
| DI-DN500-PN40 | 13565
Sub-total
| Masanza storage tank | 5,000 m3
9 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO KASULU BPS | Length (m)
| DI-DN900-PN10 | 395
| DI-DN900-PN16 | 2370
| DI-DN900-PN25 | 17140
| DI-DN900-PN30 | 4399
Sub-total
10 | Kasulu BPS
a. Kasulu booster station BPS
| High-lift pump | H = 325 m, (4W+2S)@541 m3/h parallel, v = 0.945 m/s
| Sump capacity | V = 6,000 m3
| Operating time | 22 hrs
| b. Rising main from Kasulu BPS to Heru juu ST | Length (m)
| DI-DN900-PN10 | 6880
| DI-DN900-PN16 | 1645
| DI-DN900-PN25 | 1275
| DI-DN900-PN30 | 689
| DI-DN900-PN40 | 285
Sub-total
| c. Heru juu storage tank | 12,000 m3
11 | GRAVITY MAIN FROM HERU JUU ST TO HERU JUU JUNCTION | Length (m)
| DI-DN700-PN10 | 1620
12 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KITAMBUKA BPS | Length (m)
| DI-DN500-PN10 | 6620
| DI-DN500-PN16 | 3710
| DI-DN500-PN25 | 10610
| DI-DN500-PN30 | 8225
Sub-total
13 | KITAMBUKA BPS
a. Kitambuka booster station BPS
| High-lift pump | H = 140 m, (2W+1S)@374 m3/h parallel, v = 1.09 m/s
| Sump capacity | V = 3,000 m3
| b. Rising main from Kitambuka BPS to Kitambuka ST junction | Length (m)
| DI-DN500-PN10 | 405
| DI-DN500-PN16 | 905
Sub-total
| c. Rising main from Kitambuka ST junction to Kitambuka ST | Length (m)
| DI-DN350-PN10 | 240
| d. Kitambuka storage tank | 2,000 m3
| d. Rising main from Kitambuka junction to Manyovu ST | Length (m)
| DI-DN350-PN10 | 2950
| DI-DN350-PN16 | 3820
Sub-total
| c. Manyovu storage tank | 2,000 m3
14 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KIBONDO JUNCTION 01 | Length (m)
| DI-DN1000-PN10 | 6475
| DI-DN1000-PN16 | 7472
| DI-DN1000-PN25 | 15809
| DI-DN1000-PN30 | 15725
| DI-DN1000-PN40 | 21025
| DI-DN1000-PN50 | 73878
| DI-DN1000-PN60 | 13657
Sub-total
15 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO KIBONDO NEW ST | Length (m)
| DI-DN450-PN10 | 195
| DI-DN450-PN16 | 608
Sub-total
| New Kibondo storage tank | 4,000 m3
16 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO JUNCTION 02 | Length (m)
| DI-DN450-PN16 | 1580
17 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KIBONDO EXISTING ST | Length (m)
| DI-DN300-PN10 | 620
| Exising Kibondo storage tank | 1,000 m3
18 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KAKOKONKO ST | Length (m)
| DI-DN350-PN10 | 85
| DI-DN350-PN16 | 2275
| DI-DN350-PN25 | 23990
| DI-DN350-PN30 | 18325
| DI-DN350-PN40 | 5115
Sub-total
| Kakonko storage tank | 2,000 m3
KATAVI OPTION
1 | SHUKULA KAREMA INTAKE
a. Raw water pump station
| Intake Capacity | 73,593 m3/day
| Operating time | 22 hrs
| Raw water high-lift pump | H = 75 m, (4W+2S)@836 m3/h parallel, v = 1.18 m/s
| Raw water sump | V = 14,000 m3
| b. Raw water rising main to Shukula Karema WTP | Length (m)
| DI-DN1000-PN10 | 380
2 | SHUKULA KAREMA WTP
| WTP capacity | 68,441 m3/day
| Operating time | 22 hrs
| High-lift pump | H = 395 m, (4W+2S)@778 m3/h parallel, 1.01 m/s
| Clear water tank | V = 8,000 m3
3 | RISING MAIN FROM SHAKULA KAREMA WTP TO KASEKESE ST | Length (m)
| DI-DN1000-PN10 | 7405
| DI-DN1000-PN16 | 8353
| DI-DN1000-PN25 | 13153
| DI-DN1000-PN30 | 6785
| DI-DN1000-PN40 | 7920
| DI-DN1000-PN50 | 13425
Sub-total
| Kasekese storage tank | 12,000 m3
4 | GRAVITY MAIN FROM KASEKESE ST TO KAYENZE BPS | Length (m)
| DI-DN1000-PN10 | 12432
| DI-DN1000-PN16 | 15757
Sub-total
5 | KAYENZE BPS
a. Kayenze booster station BPS
| High-lift pump | H = 405 m, (4W+2S)@778 m3/h parallel, 1.01 m/s
| Sump capacity | V = 8,000 m3
b. Kayenze BPS to Kayenze ST
| DI-DN1000-PN10 | 597
| DI-DN1000-PN16 | 350
| DI-DN1000-PN25 | 360
| DI-DN1000-PN30 | 243
| DI-DN1000-PN40 | 349
| DI-DN1000-PN50 | 225
Sub-total
| c. Kayenze Storage Tank | V = 18,000 m3
6 | GRAVITY MAIN FROM KAYENZE ST TO MPANDA JUNCTION 02
| DI-DN900-PN10 | 620
| DI-DN900-PN16 | 325
| DI-DN900-PN25 | 390
| DI-DN900-PN30 | 259
| DI-DN900-PN40 | 9868
| DI-DN900-PN50 | 34856
| DI-DN900-PN60 | 22808
Sub-total
7 | GRAVITY MAIN FROM MPANDA JUNCTION 02 TO MILALA ST | Length (m)
| DI-DN500-PN30 | 185
| DI-DN500-PN40 | 1447
| DI-DN500-PN50 | 3978
Sub-total
| Milala storage tank | 5,000 m3
8 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MPANDA JUNCTION 2
| DI-DN700-PN50 | 2835
9 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MSANGINYA JUNCTION | Length (m)
| DI-DN500-PN25 | 13353
| DI-DN500-PN30 | 6858
Sub-total
10 | GRAVITY MAIN FROM MSANGINYA JUNCTION TO MSANGINYA ST | Length (m)
| DI-DN450-PN25 | 132
| DI-DN450-PN30 | 130
| DI-DN450-PN40 | 2500
| DI-DN450-PN50 | 715
Sub-total
| Msanginya tank | 3,000 m3
11 | GRAVITY MAIN FROM MSANGINYA JUNCTION TO INYONGA ST | Length (m)
| DI-DN400-PN16 | 20785
| DI-DN400-PN25 | 63300
| DI-DN400-PN30 | 4725
| DI-DN400-PN40 | 3155
| DI-DN400-PN50 | 18650
Sub-total
| Inyonga storage tank | 2,000 m3
12 | GRAVITY MAIN FROM MPANDA JUNCTION 01 TO KIZI BPS | Length (m)
| DI-DN500-PN10 | 7651
| DI-DN500-PN16 | 2619
| DI-DN500-PN25 | 5960
| DI-DN500-PN30 | 4772
| DI-DN500-PN40 | 17477
| DI-DN500-PN50 | 41040
Sub-total
13 | KIZI BPS
a. Kizi booster pump station
| High-lift pump | H = 215 m, (1W+1S)@ 536m3/h parallel, v = 1.01 m/s
| Sump capacity | V = 1,000 m3
| b. Rising main from Kizi BPS to Kizi ST | Length (m)
| DI-DN500-PN10 | 998
| DI-DN500-PN16 | 1565
| DI-DN500-PN25 | 7460
Sub-total
| c. Kizi storage tank | V = 2,000 m3
14 | GRAVITY MAIN FROM KIZI ST TO MAJIMOTO ST | Length (m)
| DI-DN450-PN10 | 8455
| DI-DN450-PN16 | 1950
| DI-DN450-PN25 | 1610
| DI-DN450-PN30 | 784
| DI-DN450-PN40 | 1965
| DI-DN450-PN50 | 5765
| DI-DN450-PN60 | 43347
Sub-total
| Majimoto storage tank | V = 4,000 m3
RUKWA OPTION
1 | SAMAZI INTAKE
a. Raw water pump station
| Intake Capacity | 79,087m3/day
| Operating time | 22hrs
| Raw water high-lift pump | H = 305 m, (4W+2S)@899 m3/h parallel, v = 1.27 m/s
| Raw water sump | V = 15,000 m3
| b. Raw water rising main to Samazi WTP | Length (m)
| DI-DN1000-PN10 | 1325
| DI-DN1000-PN16 | 195
| DI-DN1000-PN25 | 339
| DI-DN1000-PN30 | 431
| DI-DN1000-PN40 | 363
Sub-total
2 | SAMAZI WTP
| a. WTP capacity | 73,550 m3/day
| Operating time | 22hrs
| High-lift pump | H = 345 m, (4W+2S)@836 m3/h parallel, v = 1.182m/s
| Clear water tank | V = 15,000 m3
| b. Rising main from samazi WTP to Kafukoka BPS 01 | Length (m)
| DI-DN1000-PN10 | 2097
| DI-DN1000-PN16 | 1159
| DI-DN1000-PN25 | 5049
| DI-DN1000-PN30 | 545
| DI-DN1000-PN40 | 4573
Sub-total
3 | KAFUKOKA BPS 01
a. Kafukoka booster pump station 01
| High-lift pump | H = 345 m, (4W+2S)@836 m3/h parallel, v = 1.182m/s
| Sump capacity | V = 8,000 m3
| b. Rising main from Kafukoka BPS 01 to Mkowe BPS 2 | Length (m)
| DI-DN1000-PN10 | 4548
| DI-DN1000-PN16 | 16480
| DI-DN1000-PN25 | 2846
| DI-DN1000-PN30 | 1108
| DI-DN1000-PN40 | 870
Sub-total
4 | MKOWE BPS 02
a. Mkowe booster pump station 02
| High-lift pump | H = 295 m, (4W+2S)@836 m3/h parallel, v = 1.182m/s
| Sump capacity | V = 8,000 m3
| b. Rising main from BPS 02 to Mkowe BPS 03 | Length (m)
| DI-DN1000-PN10 | 1461
| DI-DN1000-PN16 | 14586
| DI-DN1000-PN25 | 16830
| DI-DN1000-PN30 | 14603
Sub-total
5 | MATANGA BPS 03
a. Matanga booster pump station 03
| High-lift pump | H = 245 m, (4W+2S)@836 m3/h parallel, v = 1.182m/s
| Sump capacity | V = 8,000 m3
| b. Rising main from BPS 03 to Matanga ST | Length (m)
| DI-DN1000-PN10 | 320
| DI-DN1000-PN16 | 190
| DI-DN1000-PN25 | 1548
Sub-total
| c. Matanga storage tank | 20,000 m3
6 | GRAVITY MAIN FROM MATANGA ST TO SUMBAWANGA DC JUNCTION | Length (m)
| DI-DN1000-PN10 | 320
| DI-DN1000-PN16 | 190
| DI-DN1000-PN25 | 454
Sub-total
7 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO MATAI JUNCTION | Length (m)
| DI-DN900-PN30 | 700
| DI-DN900-PN40 | 1730
Sub-total
8 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO SUMBAWANGA DC LUSAKA ST | Length (m)
| DI-DN600-PN25 | 19201
| DI-DN600-PN30 | 7399
| DI-DN600-PN40 | 7502
| DI-DN600-PN50 | 23164
| DI-DN600-PN60 | 21255
Sub-total
| Lusaka storage tank | 6,000 m3
9 | GRAVITY MAIN FROM MATAI JUNCTION TO MATAI ST | Length (m)
| DI-DN500-PN25 | 25970
| Matai storage tank | 4,000 m3
10 | GRAVITY MAIN FROM MATAI JUNCTION TO SUMBAWANGA MC JUNCTION | Length (m)
| DI-DN700-PN40 | 15040
11 | SUMBAWANGA MC JUNCTION TO SUMBAWANGA MPONDA BPS | Length (m)
| DI-DN500-PN10 | 713
| DI-DN500-PN16 | 2371
| DI-DN500-PN25 | 1634
| DI-DN500-PN30 | 1317
| DI-DN500-PN40 | 14262
Sub-total
12 | SUMBAWANGA MPONDA BPS
a. Kayenze booster station BPS
| High-lift pump | H = 85 m, (2W+1S)@428 m3/h parallel, v = 0.84 m/s
| Sump capacity | V = 2,000 m3
| b. Rising main from Mponda BPS to Mponda ST | Length (m)
| DI-DN600-PN10 | 745
| Mponda storage tank | 6,000 m3
13 | SUMBAWANGA MC JUNCTION TO CHALA ST | Length (m)
| DI-DN500-PN25 | 26063
| DI-DN500-PN30 | 17226
| DI-DN500-PN40 | 11961
Sub-total
| Chala storage tank | 6,000 m3

## OPTION 02
LT-WATSAN PROJECT
S/N | PROJECT SUMMARY - OPTION 02
KIGOMA OPTION
1 | KASEKE INTAKE
| Intake Capacity | 101,778 m3/day
a. Raw water pump station
| Operating time | 22hrs
| Raw water high-lift pump | H = 35 m, (2W+1S)@2,313 m3/h parallel, v = 1.16 m/s
| Raw water sump | V = 15,000 m3
| b. Raw water rising main to Kaseke WTP | Length (m)
| DI-DN1200-PN10 | 750
2 | KASEKE WTP
| WTP capacity | 94,653 m3/day
| Operating time | 22 hrs
| high-lift pump | H = 405 m, (6W+3S)@717 m3/h parallel, v = 1.057 m/s
| Clear water sump | V = 15,000 m3
3 | RISING MAIN FROM KASEKE WTP TO SIMBO JUNCTION | Length (m)
| DI-DN1200-PN40 | 2805
| DI-DN1200-PN50 | 14390
Sub-total
4 | RISING MAIN FROM SIMBO JUNCTION TO SIMBO ST | Length (m)
| DI-DN450-PN16 | 395
| DI-DN450-PN25 | 895
| DI-DN450-PN30 | 305
| DI-DN450-PN40 | 235
Sub-total
| Simbo storage tank | 3,000 m3
5 | RISING MAIN FROM SIMBO JUNCTION TO RUSESA BPS | Length (m)
| DI-DN1200-PN10 | 5376
| DI-DN1200-PN16 | 3159
| DI-DN1200-PN25 | 12178
| DI-DN1200-PN30 | 4585
| DI-DN1200-PN40 | 5143
Sub-total
6 | RUSESA BPS
a. Rusesa booster station BPS
| High-lift pump | H = 330 m, (6W+2S)@629 m3/h parallel, v = 0.927 m/s
| Sump capacity | V = 12,000 m3
| Operating time | 22 hrs
| b. Rising main from Rusesa BPS to Rusesa ST | Length (m)
| DI-DN1200-PN10 | 298
| DI-DN1200-PN16 | 279
| DI-DN1200-PN25 | 280
| DI-DN1200-PN30 | 2390
| DI-DN1200-PN40 | 1935
Sub-total
| Rusesa storage tank | 20,000 m3
7 | GRAVITY MAIN FROM RUSESA ST TO NYUMBIGWA JUNCTION | Length (m)
| DI-DN1000-PN10 | 400
| DI-DN1000-PN16 | 230
| DI-DN1000-PN25 | 20960
| DI-DN1000-PN30 | 3730
Sub-total
8 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO MASANZA UVINZA | Length (m)
| DI-DN500-PN16 | 1145
| DI-DN500-PN25 | 20818
| DI-DN500-PN30 | 14110
| DI-DN500-PN40 | 13565
Sub-total
| Masanza storage tank | 5,000 m3
9 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO KASULU BPS | Length (m)
| DI-DN900-PN10 | 395
| DI-DN900-PN16 | 2370
| DI-DN900-PN25 | 17140
| DI-DN900-PN30 | 4399
Sub-total
10 | Kasulu BPS
a. Kasulu booster station BPS
| High-lift pump | H = 325 m, (4W+2S)@541 m3/h parallel, v = 0.945 m/s
| Sump capacity | V = 6,000 m3
| Operating time | 22 hrs
| b. Rising main from Kasulu BPS to Heru juu ST | Length (m)
| DI-DN900-PN10 | 6880
| DI-DN900-PN16 | 1645
| DI-DN900-PN25 | 1275
| DI-DN900-PN30 | 689
| DI-DN900-PN40 | 285
Sub-total
| c. Heru juu storage tank | 12,000 m3
11 | GRAVITY MAIN FROM HERU JUU ST TO HERU JUU JUNCTION | Length (m)
| DI-DN700-PN10 | 1620
12 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KITAMBUKA BPS | Length (m)
| DI-DN500-PN10 | 6620
| DI-DN500-PN16 | 3710
| DI-DN500-PN25 | 10610
| DI-DN500-PN30 | 8225
Sub-total
13 | KITAMBUKA BPS
a. Kitambuka booster station BPS
| High-lift pump | H = 140 m, (2W+1S)@374 m3/h parallel, v = 1.09 m/s
| Sump capacity | V = 3,000 m3
| b. Rising main from Kitambuka BPS to Kitambuka ST junction | Length (m)
| DI-DN500-PN10 | 405
| DI-DN500-PN16 | 905
Sub-total
| c. Rising main from Kitambuka ST junction to Kitambuka ST | Length (m)
| DI-DN350-PN10 | 240
| d. Kitambuka storage tank | 2,000 m3
| d. Rising main from Kitambuka junction to Manyovu ST | Length (m)
| DI-DN350-PN10 | 2950
| DI-DN350-PN16 | 3820
Sub-total
| c. Manyovu storage tank | 2,000 m3
14 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KIBONDO JUNCTION 01 | Length (m)
| DI-DN1000-PN10 | 6475
| DI-DN1000-PN16 | 7472
| DI-DN1000-PN25 | 15809
| DI-DN1000-PN30 | 15725
| DI-DN1000-PN40 | 21025
| DI-DN1000-PN50 | 73878
| DI-DN1000-PN60 | 13657
Sub-total
15 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO KIBONDO NEW ST | Length (m)
| DI-DN450-PN10 | 195
| DI-DN450-PN16 | 608
Sub-total
| New Kibondo storage tank | 4,000 m3
16 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO JUNCTION 02 | Length (m)
| DI-DN450-PN16 | 1580
17 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KIBONDO EXISTING ST | Length (m)
| DI-DN300-PN10 | 620
| Exising Kibondo storage tank | 1,000 m3
18 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KAKOKONKO ST | Length (m)
| DI-DN350-PN10 | 85
| DI-DN350-PN16 | 2275
| DI-DN350-PN25 | 23990
| DI-DN350-PN30 | 18325
| DI-DN350-PN40 | 5115
Sub-total
| Kakonko storage tank | 2,000 m3
KATAVI AND RUKWA COMMON INTAKE OPTION
1 | SAMAZI INTAKE
a. Raw water pump station
| Intake Capacity | 1,218,118 m3/day
| Operating time | 24hrs
| Raw water high-lift pump | H = 300 m, (24W+12S)@2,115 m3/h parallel
| Raw water sump | V = 102,000 m3
| b. Raw water rising main to Samazi WTP | Length (m)
| DI-DN4000-PN10 | 1330
| DI-DN4000-PN16 | 194
| DI-DN4000-PN25 | 340
| DI-DN4000-PN30 | 480
| DI-DN4000-PN40 | 361
Sub-total
2 | SAMAZI WTP
| a. WTP capacity | 1,132,849 m3/day
| Operating time | 24 hrs
| High-lift pump | H = 328 m, (22W+11S)@2,146m3/h parallel, v = 1.04 m/s
| Clear water tank | V = 190,000 m3
| b. Rising main from samazi WTP to Kafukoka BPS 01 | Length (m)
| DI-DN4000-PN10 | 2145
| DI-DN4000-PN16 | 1165
| DI-DN4000-PN25 | 4365
| DI-DN4000-PN30 | 1230
| DI-DN4000-PN40 | 4520
Sub-total
3 | KAFUKOKA BPS 01
a. Kafukoka booster pump station 01
| High-lift pump | H = 315m, (22W+11S)@2,146 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from Kafukoka BPS 01 to Mkowe BPS 2 | Length (m)
| DI-DN4000-PN10 | 4598
| DI-DN4000-PN16 | 10408
| DI-DN4000-PN25 | 8785
| DI-DN4000-PN30 | 1475
| DI-DN4000-PN40 | 590
Sub-total
4 | MKOWE BPS 02
a. Mkowe booster pump station 02
| High-lift pump | H = 240 m, (22W+11S)@2,146 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from BPS 02 to Mkowe BPS 03 | Length (m)
| DI-DN4000-PN10 | 1585
| DI-DN4000-PN16 | 14955
| DI-DN4000-PN25 | 18780
| DI-DN4000-PN30 | 12210
Sub-total
5 | MATANGA BPS 03
a. Matanga booster pump station 03
| High-lift pump | H = 235 m, (22W+11S)@2,149 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from BPS 03 to Matanga ST | Length (m)
| DI-DN4000-PN10 | 320
| DI-DN4000-PN16 | 190
| DI-DN4000-PN25 | 485
Sub-total
| c. Matanga storage tank | 284,000 m3
6 | GRAVITY MAIN FROM MATANGA ST TO SUMBAWANGA DC JUNCTION | Length (m)
| DI-DN4000-PN10 | 285
| DI-DN4000-PN16 | 180
| DI-DN4000-PN25 | 418
Sub-total
7 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO MATAI JUNCTION | Length (m)
| DI-DN3800-PN30 | 730
| DI-DN3800-PN40 | 1795
Sub-total
8 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO SUMBAWANGA DC LUSAKA ST | Length (m)
| DI-DN1400-PN25 | 19109
| DI-DN1400-PN30 | 7420
| DI-DN1400-PN40 | 7430
| DI-DN1400-PN50 | 20560
| DI-DN1400-PN60 | 23930
Sub-total
| Lusaka storage tank | 33,000 m3
9 | GRAVITY MAIN FROM MATAI JUNCTION TO MATAI ST | Length (m)
| DI-DN1200-PN40 | 25970
| Matai storage tank | 21,000 m3
10 | GRAVITY MAIN FROM MATAI JUNCTION TO SUMBAWANGA MC JUNCTION | Length (m)
| DI-DN3600-PN40 | 15040
11 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO SUMBAWANGA MPONDA BPS | Length (m)
| DI-DN1200-PN10 | 713
| DI-DN1200-PN16 | 2371
| DI-DN1200-PN25 | 1634
| DI-DN1200-PN30 | 1317
| DI-DN1200-PN40 | 14262
Sub-total
12 | SUMBAWANGA MPONDA BPS
a. Kayenze booster station BPS
| High-lift pump | H = 55 m, (4W+2S)@1,171 m3/h parallel, v = 1.0 m/s
| Sump capacity | V = 10,000 m3
| b. Rising main from Mponda BPS to Mponda ST | Length (m)
| DI-DN1200-PN10 | 745
| Mponda storage tank | 28,000 m3
13 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO CHALA JUNCTION | Length (m)
| DI-DN3400-PN25 | 11628
| DI-DN3400-PN30 | 22559
| DI-DN3400-PN40 | 13285
| DI-DN3400-PN50 | 460
Sub-total
14 | GRAVITY MAIN FROM CHALA JUNCTION TO CHALA ST | Length (m)
| DI-DN1200-PN25 | 130
| DI-DN1200-PN30 | 135
| DI-DN1200-PN40 | 395
Sub-total
15 | GRAVITY MAIN FROM CHALA JUNCTION TO KIZI JUNCTION | Length (m)
| DI-DN3000-PN40 | 898
| DI-DN3000-PN50 | 21965
| DI-DN3000-PN60 | 12650
| DI-DN3000-PN70 | 18118
| DI-DN3000-PN80 | 620
Sub-total
16 | GRAVITY MAIN FROM KIZI JUNCTION TO KIZI BPT | Length (m)
| DI-DN1200-PN70 | 4545
| DI-DN1200-PN80 | 1960
| DI-DN1200-PN90 | 1230
Sub-total
| Kizi BPT | 5,000 m3
17 | GRAVITY MAIN FROM KIZI BPT TO MAJIMOTO ST | Length (m)
| DI-DN1200-PN10 | 1075
| DI-DN1200-PN16 | 2460
| DI-DN1200-PN25 | 4285
| DI-DN1200-PN30 | 2678
| DI-DN1200-PN40 | 41120
Sub-total
| Majimoto ST | 30,000 m3
18 | GRAVITY MAIN FROM KIZI JUNCTION TO MPANDA JUNCTION 1 | Length (m)
| DI-DN2800-PN70 | 7775
| DI-DN2800-PN80 | 14009
| DI-DN2800-PN90 | 2625
| DI-DN2800-PN100 | 26005
| DI-DN2800-PN110 | 24770
| DI-DN2800-PN120 | 42520
Sub-total
19 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MSAGINYA JUNCTION | Length (m)
| DI-DN1600-PN100 | 15205
| DI-DN1600-PN110 | 4998
Sub-total
20 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO MSAGINYA ST | Length (m)
| DI-DN1200-PN90 | 250
| DI-DN1200-PN100 | 3220
Sub-total
| Msanginya tank | 28,000 m3
21 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO INYONGA ST | Length (m)
| DI-DN900-PN70 | 6340
| DI-DN900-PN80 | 55155
| DI-DN900-PN90 | 28260
| DI-DN900-PN100 | 14460
| DI-DN900-PN110 | 6310
Sub-total
| Inyonga storage tank | 17,000 m3
22 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MPANDA JUNCTION 2 | Length (m)
| DI-DN2400-PN110 | 2835
23 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO MILALA ST | Length (m)
| DI-DN1600-PN90 | 230
| DI-DN1600-PN100 | 1955
| DI-DN1600-PN110 | 3415
Sub-total
| Milala storage tank | 48,000 m3
24 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO KAYENZE ST | Length (m)
| DI-DN1600-PN60 | 620
| DI-DN1600-PN70 | 455
| DI-DN1600-PN80 | 475
| DI-DN1600-PN90 | 520
| DI-DN1600-PN100 | 32685
| DI-DN1600-PN110 | 34375
Sub-total
| Kayenze Storage Tank | 52,000 m3

## OPTION 03
LT-WATSAN PROJECT
S/N | PROJECT SUMMARY - OPTION 03
KIGOMA, KATAVI AND RUKWA COMMON INTAKE OPTION
1 | SAMAZI INTAKE
a. Raw water pump station
| Intake Capacity | 1,570,609 m3/day
| Operating time | 24hrs
| Raw water high-lift pump | H = 300 m, (28W+14S)@2,337 m3/h parallel, V = 0.96 m/s
| Raw water sump | V = 200,000 m3
| b. Raw water rising main to Samazi WTP | Length (m)
| DI-DN5000-PN10 | 1520
| DI-DN5000-PN16 | 198
| DI-DN5000-PN25 | 340
| DI-DN5000-PN30 | 480
| DI-DN5000-PN40 | 320
Sub-total
2 | SAMAZI WTP
| a. WTP capacity | 1,460,666 m3/day
| Operating time | 24 hrs
| High-lift pump | H = 328 m, (26W+13S)@2,341m3/h parallel, v = 1.02m/s
| Clear water tank | V = 310,000 m3
| b. Rising main from samazi WTP to Kafukoka BPS 01 | Length (m)
| DI-DN4600-PN10 | 2098
| DI-DN4600-PN16 | 1160
| DI-DN4600-PN25 | 4320
| DI-DN4600-PN30 | 1285
| DI-DN4600-PN40 | 4578
Sub-total
3 | KAFUKOKA BPS 01
a. Kafukoka booster pump station 01
| High-lift pump | H = 315m, (26W+13S)@2,341 m3/h parallel, v = 1.02 m/s
| Sump capacity | V = 130,000 m3
| b. Rising main from Kafukoka BPS 01 to Mkowe BPS 2 | Length (m)
| DI-DN4600-PN10 | 4505
| DI-DN4600-PN16 | 10305
| DI-DN4600-PN25 | 8940
| DI-DN4600-PN30 | 1475
| DI-DN4600-PN40 | 635
Sub-total
4 | MKOWE BPS 02
a. Mkowe booster pump station 02
| High-lift pump | H = 237 m, (26W+13S)@2,341 m3/h parallel, v = 1.02 m/s
| Sump capacity | V = 130,000 m3
| b. Rising main from BPS 02 to Mkowe BPS 03 | Length (m)
| DI-DN4600-PN10 | 1575
| DI-DN4600-PN16 | 15225
| DI-DN4600-PN25 | 18920
| DI-DN4600-PN30 | 11770
Sub-total
5 | MATANGA BPS 03
a. Matanga booster pump station 03
| High-lift pump | H = 235 m, (26W+13S)@2,341m3/h parallel, v = 1.02 m/s
| Sump capacity | V = 130,000 m3
| b. Rising main from BPS 03 to Matanga ST | Length (m)
| DI-DN4600-PN10 | 280
| DI-DN4600-PN16 | 180
| DI-DN4600-PN25 | 540
Sub-total
| c. Matanga storage tank | 365,000 m3
6 | GRAVITY MAIN FROM MATANGA ST TO SUMBAWANGA DC JUNCTION | Length (m)
| DI-DN4600-PN10 | 185
| DI-DN4600-PN16 | 260
| DI-DN4600-PN25 | 438
Sub-total
7 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO MATAI JUNCTION | Length (m)
| DI-DN4400-PN30 | 530
| DI-DN4400-PN40 | 1995
Sub-total
8 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO SUMBAWANGA DC LUSAKA ST | Length (m)
| DI-DN1400-PN25 | 18109
| DI-DN1400-PN30 | 7920
| DI-DN1400-PN40 | 7930
| DI-DN1400-PN50 | 20060
| DI-DN1400-PN60 | 24430
Sub-total
| Lusaka storage tank | 33,000 m3
9 | GRAVITY MAIN FROM MATAI JUNCTION TO MATAI ST | Length (m)
| DI-DN1200-PN40 | 25970
| Matai storage tank | 21,000 m3
10 | GRAVITY MAIN FROM MATAI JUNCTION TO SUMBAWANGA MC JUNCTION | Length (m)
| DI-DN4200-PN40 | 15040
11 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO SUMBAWANGA MPONDA BPS | Length (m)
| DI-DN1200-PN10 | 713
| DI-DN1200-PN16 | 2371
| DI-DN1200-PN25 | 1634
| DI-DN1200-PN30 | 1317
| DI-DN1200-PN40 | 14262
Sub-total
12 | SUMBAWANGA MPONDA BPS
a. Kayenze booster station BPS
| High-lift pump | H = 55 m, (4W+2S)@1,171 m3/h parallel, v = 1.0 m/s
| Sump capacity | V = 10,000 m3
| b. Rising main from Mponda BPS to Mponda ST | Length (m)
| DI-DN1200-PN10 | 745
| Mponda storage tank | 28,000 m3
13 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO CHALA JUNCTION | Length (m)
| DI-DN4000-PN25 | 10100
| DI-DN4000-PN30 | 23060
| DI-DN4000-PN40 | 13745
| DI-DN4000-PN50 | 1020
Sub-total
14 | GRAVITY MAIN FROM CHALA JUNCTION TO CHALA ST | Length (m)
| DI-DN1200-PN25 | 130
| DI-DN1200-PN30 | 135
| DI-DN1200-PN40 | 395
Sub-total
15 | GRAVITY MAIN FROM CHALA JUNCTION TO KIZI JUNCTION | Length (m)
| DI-DN3800-PN40 | 670
| DI-DN3800-PN50 | 20210
| DI-DN3800-PN60 | 12190
| DI-DN3800-PN70 | 15970
| DI-DN3800-PN80 | 5198
Sub-total
16 | GRAVITY MAIN FROM KIZI JUNCTION TO KIZI BPT | Length (m)
| DI-DN1200-PN70 | 4345
| DI-DN1200-PN80 | 1990
| DI-DN1200-PN90 | 1400
Sub-total
| Kizi BPT | 5,000 m3
17 | GRAVITY MAIN FROM KIZI BPT TO MAJIMOTO ST | Length (m)
| DI-DN1200-PN10 | 975
| DI-DN1200-PN16 | 2360
| DI-DN1200-PN25 | 4185
| DI-DN1200-PN30 | 2678
| DI-DN1200-PN40 | 41320
Sub-total
| Majimoto ST | 30,000 m3
18 | GRAVITY MAIN FROM KIZI JUNCTION TO MPANDA JUNCTION 1 | Length (m)
| DI-DN3600-PN60 | 820
| DI-DN3600-PN70 | 7825
| DI-DN3600-PN80 | 13510
| DI-DN3600-PN90 | 3195
| DI-DN3600-PN100 | 21965
| DI-DN3600-PN110 | 27050
| DI-DN3600-PN120 | 44280
Sub-total
19 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MSAGINYA JUNCTION | Length (m)
| DI-DN1600-PN100 | 10205
| DI-DN1600-PN110 | 9998
Sub-total
20 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO MSAGINYA ST | Length (m)
| DI-DN1200-PN90 | 150
| DI-DN1200-PN100 | 3220
Sub-total
| Msanginya tank | 28,000 m3
21 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO INYONGA ST | Length (m)
| DI-DN900-PN70 | 5340
| DI-DN900-PN80 | 54155
| DI-DN900-PN90 | 29260
| DI-DN900-PN100 | 13460
| DI-DN900-PN110 | 8310
Sub-total
| Inyonga storage tank | 17,000 m3
22 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MPANDA JUNCTION 2 | Length (m)
| DI-DN3200-PN110 | 2835
23 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO MILALA ST | Length (m)
| DI-DN1600-PN90 | 130
| DI-DN1600-PN100 | 1955
| DI-DN1600-PN110 | 3515
Sub-total
| Milala storage tank | 48,000 m3
24 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO KAREMA JUNCTION | Length (m)
| DI-DN2800-PN100 | 7330
| DI-DN2800-PN110 | 3265
Sub-total
25 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO KAYENZE ST | Length (m)
| DI-DN1600-PN60 | 620
| DI-DN1600-PN70 | 455
| DI-DN1600-PN80 | 475
| DI-DN1600-PN90 | 520
| DI-DN1600-PN100 | 32685
| DI-DN1600-PN110 | 34375
Sub-total
| Kayenze Storage Tank | 52,000 m3
26 | GRAVITY MAIN FROM KAREMA JUNCTION TO MASANZA UVINZA JUNCTION | Length (m)
| DI-DN2200-PN40 | 9600
| DI-DN2200-PN50 | 13635
| DI-DN2200-PN60 | 12545
| DI-DN2200-PN70 | 26105
| DI-DN2200-PN80 | 48300
| DI-DN2200-PN90 | 36293
| DI-DN2200-PN100 | 36055
| DI-DN2200-PN110 | 11120
Sub-total
27 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO MASANZA UVINZA | Length (m)
| DI-DN1400-PN90 | 2125
| Masanza storage tank | 15,000 m3
28 | GRAVITY MAIN FROM MASANZA JUNCTION TO NYUMBIGWA UVINZA | Length (m)
| DI-DN2000-PN60 | 2050
| DI-DN2000-PN70 | 3545
| DI-DN2000-PN80 | 2335
| DI-DN2000-PN90 | 23985
| DI-DN2000-PN100 | 21095
Sub-total
29 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO RUSESA ST JUNCTION | Length (m)
| DI-DN1200-PN80 | 24260
30 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO RUSESA ST | Length (m)
| DI-DN1000-PN60 | 245
| DI-DN1000-PN70 | 425
| DI-DN1000-PN80 | 395
Sub-total
| Rusesa storage tank | 30,000 m3
31 | GRAVITY MAIN FROM RUSESA ST JUNCTION TO LOLAWAHA SIMBO ST | Length (m)
| DI-DN800-PN80 | 1205
| DI-DN800-PN90 | 6815
| DI-DN800-PN100 | 11735
| DI-DN800-PN110 | 14690
| DI-DN800-PN120 | 1780
Sub-total
| Lolawaha storage tank | 10,000 m3
32 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO HERU JUU JUNCTION | Length (m)
| DI-DN1400-PN30 | 4165
| DI-DN1400-PN40 | 2680
| DI-DN1400-PN50 | 1448
| DI-DN1400-PN60 | 855
| DI-DN1400-PN70 | 2630
| DI-DN1400-PN80 | 16227
| DI-DN1400-PN90 | 5448
Sub-total
33 | GRAVITY MAIN FROM HERU JUU JUNCTION TO HERU JUU ST | Length (m)
| DI-DN1200-PN30 | 1625
| Heru juu storage tank | 30,000 m3
34 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KITAMBUKA JUNCTION | Length (m)
| DI-DN900-PN30 | 1182
| DI-DN900-PN40 | 7150
| DI-DN900-PN50 | 5505
| DI-DN900-PN60 | 16710
Sub-total
35 | GRAVITY MAIN FROM KITAMBUKA JUNCTION TO KITAMBUKA ST | Length (m)
| DI-DN600-PN40 | 235
| Kitambuka storage tank | 8,000 m3
36 | GRAVITY MAIN FROM KITAMBUKA JUNCTION TO MANYOVU JUNCTION | Length (m)
| DI-DN600-PN25 | 3015
| DI-DN600-PN30 | 3208
| DI-DN600-PN40 | 565
Sub-total
| c. Manyovu storage tank | 7,000 m3
37 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KIBONDO JUNCTION 01 | Length (m)
| DI-DN1000-PN10 | 6505
| DI-DN1000-PN16 | 3508
| DI-DN1000-PN25 | 12505
| DI-DN1000-PN30 | 17380
| DI-DN1000-PN40 | 24820
| DI-DN1000-PN50 | 65515
| DI-DN1000-PN60 | 23810
Sub-total
38 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO KIBONDO NEW ST | Length (m)
| DI-DN600-PN10 | 195
| DI-DN600-PN16 | 608
Sub-total
| New Kibondo storage tank | 7,000 m3
39 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO JUNCTION 02 | Length (m)
| DI-DN700-PN16 | 1580
40 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KIBONDO EXISTING ST | Length (m)
| DI-DN500-PN10 | 620
| Exising Kibondo storage tank | 1,000 m3
41 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KAKOKONKO ST | Length (m)
| DI-DN600-PN10 | 85
| DI-DN600-PN16 | 2275
| DI-DN600-PN25 | 23990
| DI-DN600-PN30 | 18325
| DI-DN600-PN40 | 5115
Sub-total
| Kakonko storage tank | 6,000 m3

## OPTION 04
LT-WATSAN PROJECT
S/N | PROJECT SUMMARY - OPTION 04
KIGOMA OPTION
1 | MALAGARASI-UGALLA CONFLUENCE INTAKE
a. Raw water pump station
| Intake Capacity | 352,492 m3/day
| Operating time | 24hrs
| Raw water high-lift pump | H = 98 m, (8W+4S)@1,836 m3/h parallel, v = 1.073 m/s
| Raw water sump | V = 60,000 m3
| b. Raw water rising main to Malagarasi Mpeta B WTP | Length (m)
| DI-DN2200-PN10 | 740
| DI-DN2200-PN16 | 1825
Sub-total
2 | MALAGARASI, MPETA WTP
| WTP capacity | 327,817 m3/day
| Operating time | 24 hrs
| Clear water sump | V = 70,000 m3
3 | GRAVITY MAIN FROM MALAGARASI MPETA WTP TO CHAKULU BPS | Length (m)
| DI-DN2200-PN10 | 24270
| DI-DN2200-PN16 | 4709
Sub-total
4 | CHAKULU BPS
a. Chakulu booster station BPS
| High-lift pump | H = 150 m, (8W+4S)@1,717m3/h parallel, v = 1.00 m/s
| Sump capacity | V = 50,000 m3
5 | RISING MAIN FROM CHAKULU BPS TO MASANZA ST | Length (m)
| DI-DN2200-PN10 | 4190
| DI-DN2200-PN16 | 5455
| DI-DN2200-PN25 | 16625
| DI-DN2200-PN30 | 2100
Sub-total
| Masanza storage tank | 90,000 m3
6 | GRAVITY MAIN FROM MASANZA ST TO MUTINDE BPS | Length (m)
| DI-DN2000-PN10 | 15378
| DI-DN2000-PN16 | 19785
| DI-DN2000-PN25 | 6750
Sub-total
7 | MUTINDE BPS
a. Mutinde booster pump station BPS Pumping to Rusesa ST
| High-lift pump | H = 285 m, (6W+3S)@739m3/h parallel, v = 1.09 m/s
| Sump capacity | V = 25,000 m3
b. Mutinde booster pump station BPS Pumping to Kasulu BPS
| High-lift pump | H = 220 m, (6W+3S)@1,145m3/h parallel, v = 1.24 m/s
| Sump capacity | V = 25,000 m3
8 | GRAVITY MAIN FROM MUTINDE BPS TO RUSESA ST | Length (m)
| DI-DN1200-PN10 | 298
| DI-DN1200-PN16 | 278
| DI-DN1200-PN25 | 10078
| DI-DN1200-PN30 | 18254
| DI-DN1200-PN40 | 4298
Sub-total
| Rusesa storage tank | 30,000 m3
9 | GRAVITY MAIN FROM RUSESA ST TO LOLAWAHA SIMBO ST | Length (m)
| DI-DN800-PN80 | 1205
| DI-DN800-PN90 | 6815
| DI-DN800-PN100 | 11735
| DI-DN800-PN110 | 14690
| DI-DN800-PN120 | 1780
Sub-total
| Lolawaha storage tank | 10,000 m3
10 | RISING MAIN FROM MUTINDE BPS TO KASULU BPS | Length (m)
| DI-DN1400-PN10 | 660
| DI-DN1400-PN16 | 2545
| DI-DN1400-PN25 | 28975
Sub-total
11 | Kasulu BPS
a. Kasulu booster station BPS
| High-lift pump | H = 325 m, (6W+3S)@1,145 m3/h parallel, v = 1.24 m/s
| Sump capacity | V = 28,000 m3
| b. Rising main from Kasulu BPS to Heru juu ST | Length (m)
| DI-DN1400-PN10 | 5962
| DI-DN1400-PN16 | 2433
| DI-DN1400-PN25 | 950
| DI-DN1400-PN30 | 1033
| DI-DN1400-PN40 | 378
Sub-total
| c. Heru juu storage tank | 42,000 m3
12 | GRAVITY MAIN FROM HERU JUU ST TO HERU JUU JUNCTION | Length (m)
| DI-DN1400-PN10 | 1620
13 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KITAMBUKA BPS | Length (m)
| DI-DN900-PN10 | 5920
| DI-DN900-PN16 | 3833
| DI-DN900-PN25 | 7310
| DI-DN900-PN30 | 12105
Sub-total
14 | KITAMBUKA BPS
a. Kitambuka booster station BPS
| High-lift pump | H = 128 m, (4W+2S)@594 m3/h parallel, v = 0.84 m/s
| Sump capacity | V = 5,000 m3
| b. Rising main from Kitambuka BPS to Kitambuka ST junction | Length (m)
| DI-DN900-PN10 | 450
| DI-DN900-PN16 | 948
| DI-DN900-PN25 | 950
Sub-total
| c. Rising main from Kitambuka ST junction to Kitambuka ST | Length (m)
| DI-DN600-PN10 | 240
| d. Kitambuka storage tank | 8,000 m3
| d. Rising main from Kitambuka junction to Manyovu ST | Length (m)
| DI-DN600-PN10 | 2610
| DI-DN600-PN16 | 4163
Sub-total
| c. Manyovu storage tank | 7,000 m3
15 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KIBONDO JUNCTION 01 | Length (m)
| DI-DN1000-PN10 | 6505
| DI-DN1000-PN16 | 3508
| DI-DN1000-PN25 | 12505
| DI-DN1000-PN30 | 17380
| DI-DN1000-PN40 | 24820
| DI-DN1000-PN50 | 65515
| DI-DN1000-PN60 | 23810
Sub-total
16 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO KIBONDO NEW ST | Length (m)
| DI-DN600-PN10 | 195
| DI-DN600-PN16 | 608
Sub-total
| New Kibondo storage tank | 7,000 m3
17 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO JUNCTION 02 | Length (m)
| DI-DN700-PN16 | 1580
18 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KIBONDO EXISTING ST | Length (m)
| DI-DN500-PN10 | 620
| Exising Kibondo storage tank | 1,000 m3
19 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KAKOKONKO ST | Length (m)
| DI-DN600-PN10 | 85
| DI-DN600-PN16 | 2275
| DI-DN600-PN25 | 23990
| DI-DN600-PN30 | 18325
| DI-DN600-PN40 | 5115
Sub-total
| Kakonko storage tank | 6,000 m3
KATAVI AND RUKWA COMMON INTAKE OPTION
1 | SAMAZI INTAKE
a. Raw water pump station
| Intake Capacity | 1,218,118 m3/day
| Operating time | 24hrs
| Raw water high-lift pump | H = 300 m, (24W+12S)@2,115 m3/h parallel
| Raw water sump | V = 120,000 m3
| b. Raw water rising main to Samazi WTP | Length (m)
| DI-DN4000-PN10 | 1330
| DI-DN4000-PN16 | 194
| DI-DN4000-PN25 | 340
| DI-DN4000-PN30 | 480
| DI-DN4000-PN40 | 361
Sub-total
2 | SAMAZI WTP
| a. WTP capacity | 1,132,849 m3/day
| Operating time | 24 hrs
| High-lift pump | H = 328 m, (22W+11S)@2,146m3/h parallel, v = 1.04 m/s
| Clear water tank | V = 190,000 m3
| b. Rising main from samazi WTP to Kafukoka BPS 01 | Length (m)
| DI-DN4000-PN10 | 2145
| DI-DN4000-PN16 | 1165
| DI-DN4000-PN25 | 4365
| DI-DN4000-PN30 | 1230
| DI-DN4000-PN40 | 4520
Sub-total
3 | KAFUKOKA BPS 01
a. Kafukoka booster pump station 01
| High-lift pump | H = 315m, (22W+11S)@2,146 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from Kafukoka BPS 01 to Mkowe BPS 2 | Length (m)
| DI-DN4000-PN10 | 4598
| DI-DN4000-PN16 | 10408
| DI-DN4000-PN25 | 8785
| DI-DN4000-PN30 | 1475
| DI-DN4000-PN40 | 590
Sub-total
4 | MKOWE BPS 02
a. Mkowe booster pump station 02
| High-lift pump | H = 240 m, (22W+11S)@2,146 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from BPS 02 to Mkowe BPS 03 | Length (m)
| DI-DN4000-PN10 | 1585
| DI-DN4000-PN16 | 14955
| DI-DN4000-PN25 | 18780
| DI-DN4000-PN30 | 12210
Sub-total
5 | MATANGA BPS 03
a. Matanga booster pump station 03
| High-lift pump | H = 235 m, (22W+11S)@2,149 m3/h parallel, v = 1.04 m/s
| Sump capacity | V = 100,000 m3
| b. Rising main from BPS 03 to Matanga ST | Length (m)
| DI-DN4000-PN10 | 320
| DI-DN4000-PN16 | 190
| DI-DN4000-PN25 | 485
Sub-total
| c. Matanga storage tank | 284,000 m3
6 | GRAVITY MAIN FROM MATANGA ST TO SUMBAWANGA DC JUNCTION | Length (m)
| DI-DN4000-PN10 | 285
| DI-DN4000-PN16 | 180
| DI-DN4000-PN25 | 418
Sub-total
7 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO MATAI JUNCTION | Length (m)
| DI-DN3800-PN30 | 730
| DI-DN3800-PN40 | 1795
Sub-total
8 | GRAVITY MAIN FROM SUMBAWANGA DC JUNCTION TO SUMBAWANGA DC LUSAKA ST | Length (m)
| DI-DN1400-PN25 | 19109
| DI-DN1400-PN30 | 7420
| DI-DN1400-PN40 | 7430
| DI-DN1400-PN50 | 20560
| DI-DN1400-PN60 | 23930
Sub-total
| Lusaka storage tank | 33,000 m3
9 | GRAVITY MAIN FROM MATAI JUNCTION TO MATAI ST | Length (m)
| DI-DN3600-PN40 | 25970
| Matai storage tank | 21,000 m3
10 | GRAVITY MAIN FROM MATAI JUNCTION TO SUMBAWANGA MC JUNCTION | Length (m)
| DI-DN3600-PN40 | 15040
11 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO SUMBAWANGA MPONDA BPS | Length (m)
| DI-DN1200-PN10 | 713
| DI-DN1200-PN16 | 2371
| DI-DN1200-PN25 | 1634
| DI-DN1200-PN30 | 1317
| DI-DN1200-PN40 | 14262
Sub-total
12 | SUMBAWANGA MPONDA BPS
a. Kayenze booster station BPS
| High-lift pump | H = 55 m, (4W+2S)@1,171 m3/h parallel, v = 1.0 m/s
| Sump capacity | V = 10,000 m3
| b. Rising main from Mponda BPS to Mponda ST | Length (m)
| DI-DN1200-PN10 | 745
| Mponda storage tank | 28,000 m3
13 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO CHALA JUNCTION | Length (m)
| DI-DN3400-PN25 | 11628
| DI-DN3400-PN30 | 22559
| DI-DN3400-PN40 | 13285
| DI-DN3400-PN50 | 460
Sub-total
14 | GRAVITY MAIN FROM CHALA JUNCTION TO CHALA ST | Length (m)
| DI-DN1200-PN25 | 130
| DI-DN1200-PN30 | 135
| DI-DN1200-PN40 | 395
Sub-total
15 | GRAVITY MAIN FROM CHALA JUNCTION TO KIZI JUNCTION | Length (m)
| DI-DN3000-PN40 | 898
| DI-DN3000-PN50 | 21965
| DI-DN3000-PN60 | 12650
| DI-DN3000-PN70 | 18118
| DI-DN3000-PN80 | 620
Sub-total
16 | GRAVITY MAIN FROM KIZI JUNCTION TO KIZI BPT | Length (m)
| DI-DN1200-PN70 | 4545
| DI-DN1200-PN80 | 1960
| DI-DN1200-PN90 | 1230
Sub-total
| Kizi BPT | 5,000 m3
17 | GRAVITY MAIN FROM KIZI BPT TO MAJIMOTO ST | Length (m)
| DI-DN1200-PN10 | 1075
| DI-DN1200-PN16 | 2460
| DI-DN1200-PN25 | 4285
| DI-DN1200-PN30 | 2678
| DI-DN1200-PN40 | 41120
Sub-total
| Majimoto ST | 30,000 m3
18 | GRAVITY MAIN FROM KIZI JUNCTION TO MPANDA JUNCTION 1 | Length (m)
| DI-DN2800-PN70 | 7775
| DI-DN2800-PN80 | 14009
| DI-DN2800-PN90 | 2625
| DI-DN2800-PN100 | 26005
| DI-DN2800-PN110 | 24770
| DI-DN2800-PN120 | 42520
Sub-total
19 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MSAGINYA JUNCTION | Length (m)
| DI-DN1600-PN100 | 15205
| DI-DN1600-PN110 | 4998
Sub-total
20 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO MSAGINYA ST | Length (m)
| DI-DN1200-PN90 | 250
| DI-DN1200-PN100 | 3220
Sub-total
| Msanginya tank | 28,000 m3
21 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO INYONGA ST | Length (m)
| DI-DN900-PN70 | 6340
| DI-DN900-PN80 | 55155
| DI-DN900-PN90 | 28260
| DI-DN900-PN100 | 14460
| DI-DN900-PN110 | 6310
Sub-total
| Inyonga storage tank | 17,000 m3
22 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MPANDA JUNCTION 2 | Length (m)
| DI-DN2400-PN110 | 2835
23 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO MILALA ST | Length (m)
| DI-DN1600-PN90 | 230
| DI-DN1600-PN100 | 1955
| DI-DN1600-PN110 | 3415
Sub-total
| Milala storage tank | 48,000 m3
24 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO KAYENZE ST | Length (m)
| DI-DN1600-PN60 | 620
| DI-DN1600-PN70 | 455
| DI-DN1600-PN80 | 475
| DI-DN1600-PN90 | 520
| DI-DN1600-PN100 | 32685
| DI-DN1600-PN110 | 34375
Sub-total
| Kayenze Storage Tank | 52,000 m3

## OPTION 05
LT-WATSAN PROJECT
S/N | PROJECT SUMMARY - OPTION 05
KIGOMA OPTION
1 | KASEKE INTAKE
| Intake Capacity | 101,778 m3/day
a. Raw water pump station
| Operating time | 22hrs
| Raw water high-lift pump | H = 35 m, (2W+1S)@2,313 m3/h parallel, v = 1.16 m/s
| Raw water sump | V = 15,000 m3
| b. Raw water rising main to Kaseke WTP | Length (m)
| DI-DN1200-PN10 | 750
2 | KASEKE WTP
| WTP capacity | 94,653 m3/day
| Operating time | 22 hrs
| high-lift pump | H = 405 m, (6W+3S)@717 m3/h parallel, v = 1.057 m/s
| Clear water sump | V = 15,000 m3
3 | RISING MAIN FROM KASEKE WTP TO SIMBO JUNCTION | Length (m)
| DI-DN1200-PN40 | 2805
| DI-DN1200-PN50 | 14390
Sub-total
4 | RISING MAIN FROM SIMBO JUNCTION TO SIMBO ST | Length (m)
| DI-DN450-PN16 | 395
| DI-DN450-PN25 | 895
| DI-DN450-PN30 | 305
| DI-DN450-PN40 | 235
Sub-total
| Simbo storage tank | 3,000 m3
5 | RISING MAIN FROM SIMBO JUNCTION TO RUSESA BPS | Length (m)
| DI-DN1200-PN10 | 5376
| DI-DN1200-PN16 | 3159
| DI-DN1200-PN25 | 12178
| DI-DN1200-PN30 | 4585
| DI-DN1200-PN40 | 5143
Sub-total
6 | RUSESA BPS
a. Rusesa booster station BPS
| High-lift pump | H = 330 m, (6W+2S)@629 m3/h parallel, v = 0.927 m/s
| Sump capacity | V = 12,000 m3
| Operating time | 22 hrs
| b. Rising main from Rusesa BPS to Rusesa ST | Length (m)
| DI-DN1200-PN10 | 298
| DI-DN1200-PN16 | 279
| DI-DN1200-PN25 | 280
| DI-DN1200-PN30 | 2390
| DI-DN1200-PN40 | 1935
Sub-total
| Rusesa storage tank | 20,000 m3
7 | GRAVITY MAIN FROM RUSESA ST TO NYUMBIGWA JUNCTION | Length (m)
| DI-DN1000-PN10 | 400
| DI-DN1000-PN16 | 230
| DI-DN1000-PN25 | 20960
| DI-DN1000-PN30 | 3730
Sub-total
8 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO MASANZA UVINZA | Length (m)
| DI-DN500-PN16 | 1145
| DI-DN500-PN25 | 20818
| DI-DN500-PN30 | 14110
| DI-DN500-PN40 | 13565
Sub-total
| Masanza storage tank | 5,000 m3
9 | GRAVITY MAIN FROM NYUMBIGWA JUNCTION TO KASULU BPS | Length (m)
| DI-DN900-PN10 | 395
| DI-DN900-PN16 | 2370
| DI-DN900-PN25 | 17140
| DI-DN900-PN30 | 4399
Sub-total
10 | Kasulu BPS
a. Kasulu booster station BPS
| High-lift pump | H = 325 m, (4W+2S)@541 m3/h parallel, v = 0.945 m/s
| Sump capacity | V = 6,000 m3
| Operating time | 22 hrs
| b. Rising main from Kasulu BPS to Heru juu ST | Length (m)
| DI-DN900-PN10 | 6880
| DI-DN900-PN16 | 1645
| DI-DN900-PN25 | 1275
| DI-DN900-PN30 | 689
| DI-DN900-PN40 | 285
Sub-total
| c. Heru juu storage tank | 12,000 m3
11 | GRAVITY MAIN FROM HERU JUU ST TO HERU JUU JUNCTION | Length (m)
| DI-DN700-PN10 | 1620
12 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KITAMBUKA BPS | Length (m)
| DI-DN500-PN10 | 6620
| DI-DN500-PN16 | 3710
| DI-DN500-PN25 | 10610
| DI-DN500-PN30 | 8225
Sub-total
13 | KITAMBUKA BPS
a. Kitambuka booster station BPS
| High-lift pump | H = 140 m, (2W+1S)@374 m3/h parallel, v = 1.09 m/s
| Sump capacity | V = 3,000 m3
| b. Rising main from Kitambuka BPS to Kitambuka ST junction | Length (m)
| DI-DN500-PN10 | 405
| DI-DN500-PN16 | 905
Sub-total
| c. Rising main from Kitambuka ST junction to Kitambuka ST | Length (m)
| DI-DN350-PN10 | 240
| d. Kitambuka storage tank | 2,000 m3
| d. Rising main from Kitambuka junction to Manyovu ST | Length (m)
| DI-DN350-PN10 | 2950
| DI-DN350-PN16 | 3820
Sub-total
| c. Manyovu storage tank | 2,000 m3
14 | GRAVITY MAIN FROM HERU JUU JUNCTION TO KIBONDO JUNCTION 01 | Length (m)
| DI-DN1000-PN10 | 6475
| DI-DN1000-PN16 | 7472
| DI-DN1000-PN25 | 15809
| DI-DN1000-PN30 | 15725
| DI-DN1000-PN40 | 21025
| DI-DN1000-PN50 | 73878
| DI-DN1000-PN60 | 13657
Sub-total
15 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO KIBONDO NEW ST | Length (m)
| DI-DN450-PN10 | 195
| DI-DN450-PN16 | 608
Sub-total
| New Kibondo storage tank | 4,000 m3
16 | GRAVITY MAIN FROM KIBONDO JUNCTION 01 TO JUNCTION 02 | Length (m)
| DI-DN450-PN16 | 1580
17 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KIBONDO EXISTING ST | Length (m)
| DI-DN300-PN10 | 620
| Exising Kibondo storage tank | 1,000 m3
18 | GRAVITY MAIN FROM KIBONDO JUNCTION 02 TO KAKOKONKO ST | Length (m)
| DI-DN350-PN10 | 85
| DI-DN350-PN16 | 2275
| DI-DN350-PN25 | 23990
| DI-DN350-PN30 | 18325
| DI-DN350-PN40 | 5115
Sub-total
| Kakonko storage tank | 2,000 m3
KATAVI AND RUKWA COMMON INTAKE OPTION
1 | KISAMBALA KIRANDO INTAKE
a. Raw water pump station
| Intake Capacity | 152,679 m3/day
| Operating time | 22 hrs
| Raw water high-lift pump | H = 145 m, (6W+3S)@1,157 m3/h parallel, v = 0.96 m/s
| Raw water sump | V = 30,000 m3
| b. Raw water rising main to Samazi WTP | Length (m)
| DI-DN1600-PN10 | 1155
| DI-DN1600-PN16 | 530
Sub-total
2 | KISAMBALA KIRANDO WTP
| a. WTP capacity | 141,991 m3/day
| Operating time | 22 hrs
| High-lift pump | H = 305 m, (8W+4S)@807 m3/h parallel, v = 0.9 m/s
| Clear water tank | V = 30,000 m3
| b. Rising main from Kisambala WTP to Lwafi-Katongoro BPS 01 | Length (m)
| DI-DN1600-PN10 | 5689
| DI-DN1600-PN16 | 1102
| DI-DN1600-PN25 | 3734
| DI-DN1600-PN30 | 1570
| DI-DN1600-PN40 | 20555
| DI-DN1600-PN50 | 5820
Sub-total
3 | LWAFI-KATONGORO BPS 01
a. Kafukoka booster pump station 01
| High-lift pump | H = 335m, (8W+4S)@807 m3/h parallel, v = 0.9 m/s
| Sump capacity | V = 30,000 m3
| b. Rising main from Lwafi-Katongoro BPS 01 to Mfili BPS 02 | Length (m)
| DI-DN1600-PN10 | 2715
| DI-DN1600-PN16 | 714
| DI-DN1600-PN25 | 4155
| DI-DN1600-PN30 | 1150
| DI-DN1600-PN40 | 4106
Sub-total
4 | Mfili BPS 02
a. Mfili booster pump station 02
| High-lift pump | H = 345m, (8W+4S)@807 m3/h parallel, v = 0.9 m/s
| Sump capacity | V = 30,000 m3
| b. Rising main from Mfili BPS 02 to Chala BPS 03 | Length (m)
| DI-DN1600-PN10 | 1320
| DI-DN1600-PN16 | 6140
| DI-DN1600-PN25 | 5635
| DI-DN1600-PN30 | 14275
| DI-DN1600-PN40 | 11872
Sub-total
5 | Chala BPS 03
a. Chala booster pump station 03
| High-lift pump | H = 345 m, (8W+4S)@807 m3/h parallel, v = 0.9 m/s
| Sump capacity | V = 30,000 m3
| b. Rising main from Chala BPS 03 to Chala ST | Length (m)
| DI-DN1600-PN10 | 1075
| DI-DN1600-PN16 | 178
| DI-DN1600-PN25 | 200
| DI-DN1600-PN30 | 70
| DI-DN1600-PN40 | 85
Sub-total
| c. Chala storage tank | 40,000 m3
6 | GRAVITY MAIN FROM CHALA ST TO CHALA JUNCTION | Length (m)
| DI-DN1600-PN10 | 1075
| DI-DN1600-PN16 | 150
| DI-DN1600-PN25 | 200
| DI-DN1600-PN30 | 70
| DI-DN1600-PN40 | 398
| DI-DN1600-PN50 | 102
Sub-total
7 | GRAVITY MAIN FROM CHALA JUNCTION TO SUMBAWANGA MC JUNCTION | Length (m)
| DI-DN1000-PN25 | 8285
| DI-DN1000-PN30 | 18513
| DI-DN1000-PN40 | 17245
| DI-DN1000-PN50 | 3885
Sub-total
8 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO SUMBAWANGA MPONDA BPS | Length (m)
| DI-DN500-PN10 | 713
| DI-DN500-PN16 | 1371
| DI-DN500-PN25 | 1634
| DI-DN500-PN30 | 1317
| DI-DN500-PN40 | 14262
Sub-total
9 | SUMBAWANGA MPONDA BPS
a. Kayenze booster station BPS
| High-lift pump | H = 85 m, (1W+1S)@856 m3/h parallel, v = 0.84 m/s
| Sump capacity | V = 3,000 m3
| b. Rising main from Mponda BPS to Mponda ST | Length (m)
| DI-DN500-PN10 | 1745
| Mponda storage tank | 5,000 m3
10 | GRAVITY MAIN FROM SUMBAWANGA MC JUNCTION TO MATAI JUNCTION | Length (m)
| DI-DN700-PN40 | 15040
11 | GRAVITY MAIN FROM MATAI JUNCTION TO SUMBAWANGA DC LUSAKA ST | Length (m)
| DI-DN600-PN25 | 22945
| DI-DN600-PN30 | 5619
| DI-DN600-PN40 | 8422
| DI-DN600-PN50 | 25870
| DI-DN600-PN60 | 18102
Sub-total
| Lusaka storage tank | 6,000 m3
12 | GRAVITY MAIN FROM MATAI JUNCTION TO MATAI ST | Length (m)
| DI-DN450-PN25 | 225
| DI-DN450-PN30 | 109
| DI-DN450-PN40 | 23198
Sub-total
| Matai storage tank | 4,000 m3
12 | GRAVITY MAIN FROM CHALA JUNCTION TO KIZI JUNCTION | Length (m)
| DI-DN1000-PN50 | 13915
| DI-DN1000-PN60 | 15975
| DI-DN1000-PN70 | 15460
| DI-DN1000-PN80 | 9065
Sub-total
13 | GRAVITY MAIN FROM KIZI JUNCTION TO KIZI BPT | Length (m)
| DI-DN400-PN70 | 4545
| DI-DN400-PN80 | 1960
| DI-DN400-PN90 | 1230
Sub-total
| Kizi BPT | 500 m3
14 | GRAVITY MAIN FROM KIZI BPT TO MAJIMOTO ST | Length (m)
| DI-DN400-PN10 | 1075
| DI-DN400-PN16 | 2460
| DI-DN400-PN25 | 4285
| DI-DN400-PN30 | 2678
| DI-DN400-PN40 | 41120
Sub-total
| Majimoto ST | 3,000 m3
15 | GRAVITY MAIN FROM KIZI JUNCTION TO MPANDA JUNCTION 1 | Length (m)
| DI-DN900-PN70 | 7775
| DI-DN900-PN80 | 14009
| DI-DN900-PN90 | 2625
| DI-DN900-PN100 | 26005
| DI-DN900-PN110 | 24770
| DI-DN900-PN120 | 42520
Sub-total
16 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MSAGINYA JUNCTION | Length (m)
| DI-DN500-PN100 | 15205
| DI-DN500-PN110 | 4998
Sub-total
17 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO MSAGINYA ST | Length (m)
| DI-DN400-PN90 | 250
| DI-DN400-PN100 | 3220
Sub-total
| Msanginya tank | 3,000 m3
18 | GRAVITY MAIN FROM MSAGINYA JUNCTION TO INYONGA ST | Length (m)
| DI-DN300-PN70 | 6340
| DI-DN300-PN80 | 55155
| DI-DN300-PN90 | 28260
| DI-DN300-PN100 | 14460
| DI-DN300-PN110 | 6310
Sub-total
| Inyonga storage tank | 2,000 m3
19 | GRAVITY MAIN FROM MPANDA JUNCTION 1 TO MPANDA JUNCTION 2 | Length (m)
| DI-DN800-PN110 | 2835
20 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO MILALA ST | Length (m)
| DI-DN500-PN90 | 230
| DI-DN500-PN100 | 1955
| DI-DN500-PN110 | 3415
Sub-total
| Milala storage tank | 5,000 m3
21 | GRAVITY MAIN FROM MPANDA JUNCTION 2 TO KAYENZE ST | Length (m)
| DI-DN500-PN60 | 620
| DI-DN500-PN70 | 455
| DI-DN500-PN80 | 475
| DI-DN500-PN90 | 520
| DI-DN500-PN100 | 32685
| DI-DN500-PN110 | 34375
Sub-total
| Kayenze Storage Tank | 5,000 m3